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AGS ROLL GROOVE SPECIFICATIONS 
For Carbon Steel Pipe And S.S Pipe
--Organized By WELPING & GruvMaster


	Actual Pipe Outside Diameter mm
	Dimensions - millimeters (mm)

	
	Pipe Outside Diameter
	Gasket Seat “A”
	Groove 
Width 
"B"
	Groove Diameter “C”
	Norminal Wall Thickness for Grooving "T"
	Max. Allow. Flare Dia. “F”

	
	Max.
	Min.
	Basic
	Max.
	Min.
	
	Max.
	Min.
	Carbon Steel
	S.S Steel Sch.10S
	

	355.6mm
	358.0
	354.8
	38.1
	38.89
	36.5
	11.6
	342.9
	341.8
	5.6–19.1
	4.8
	361.4

	377.0mm
	379.4
	376.2
	38.1
	38.89
	36.5
	11.6
	364.3
	363.2
	5.5–19.1
	–
	382.8

	406.4mm
	408.8
	405.6
	38.1
	38.89
	36.5
	11.6
	393.7
	392.6
	6.4–19.1
	4.8
	412.2

	426.0mm
	428.4
	425.2
	38.1
	38.89
	36.5
	11.6
	413.3
	412.2
	6.5–19.1
	–
	431.8

	457.2mm
	459.6
	456.4
	38.1
	38.89
	36.5
	11.6
	444.5
	443.4
	6.4–19.1
	4.8
	463.0

	480.0mm
	482.4
	479.2
	38.1
	38.89
	36.5
	11.6
	467.3
	466.2
	6.5–19.1
	–
	485.9

	508.0mm
	510.4
	507.2
	38.1
	38.89
	36.5
	11.6
	495.3
	494.2
	6.4–19.1
	5.5
	513.8

	530.0mm
	532.4
	529.2
	38.1
	38.89
	36.5
	11.6
	517.3
	516.2
	6.5–19.1
	–
	535.7

	558.8mm
	561.2
	558.0
	38.1
	38.89
	36.5
	11.6
	546.1
	545.0
	6.4–19.1
	5.5
	564.6

	609.6mm
	612.0
	608.8
	38.1
	38.89
	36.5
	11.6
	596.9
	595.8
	6.4–19.1
	5.5
	615.4

	630.0mm
	632.4
	629.2
	38.1
	38.89
	36.5
	11.6
	617.3
	616.2
	6.5–19.1
	–
	635.8

	660.4mm
	662.0
	658.8
	44.5
	45.29
	42.9
	13.6
	645.9
	644.4
	8.0–19.1
	–
	668.0

	711.2mm
	712.8
	709.6
	44.5
	45.29
	42.9
	13.6
	696.7
	695.2
	8.0–19.1
	–
	718.8

	720.0mm
	721.6
	718.4
	44.5
	45.29
	42.9
	13.6
	705.5
	704.0
	8.0–19.1
	–
	727.6

	762.0mm
	763.6
	760.4
	44.5
	45.29
	42.9
	13.6
	747.5
	746.0
	8.0–19.1
	–
	769.6

	812.8mm
	814.4
	811.2
	44.5
	45.29
	42.9
	13.6
	798.3
	796.8
	8.0–19.1
	–
	820.4

	820.0mm
	821.6
	818.4
	44.5
	45.29
	42.9
	13.6
	805.5
	804.0
	8.0–19.1
	–
	827.6

	863.6mm
	865.2
	862.0
	44.5
	45.29
	42.9
	13.6
	849.1
	847.6
	8.0–19.1
	–
	871.2

	914.4mm
	916.0
	912.8
	44.5
	45.29
	42.9
	13.6
	899.9
	898.4
	8.0–19.1
	–
	922.0

	920.0mm
	921.6
	918.4
	44.5
	45.29
	42.9
	13.6
	905.5
	904.0
	8.0–19.1
	–
	927.6

	965.0mm
	966.6
	963.4
	44.5
	45.29
	42.9
	13.6
	950.7
	949.2
	8.0–19.1
	–
	972.8

	1016.0mm
	1017.6
	1014.4
	50.8
	51.59
	49.2
	14.3
	1000.1
	998.6
	8.0–19.1
	–
	1023.6

	1066.8mm
	1068.4
	1065.2
	50.8
	51.59
	49.2
	14.3
	1050.9
	1049.4
	8.0–19.1
	–
	1074.4

	1117.6mm
	1119.2
	1116.0
	50.8
	51.59
	49.2
	14.3
	1101.7
	1100.2
	8.0–19.1
	–
	1125.2

	1168.4mm
	1170.0
	1166.8
	50.8
	51.59
	49.2
	14.3
	1152.5
	1151.0
	8.0–19.1
	–
	1176.0

	1219.2mm
	1220.8
	1217.6
	50.8
	51.59
	49.2
	14.3
	1203.3
	1201.8
	8.0–19.1
	–
	1226.8

	1270.0mm
	1271.6
	1268.4
	50.8
	51.59
	49.2
	14.3
	1254.1
	1252.6
	8.0–19.1
	–
	1277.6

	1371.6mm
	1373.2
	1370.0
	63.5
	64.29
	61.9
	14.3
	1357.1
	1355.6
	9.5–19.1
	–
	1379.2

	1422.4mm
	1424.0
	1420.8
	63.5
	64.29
	61.9
	14.3
	1407.9
	1406.4
	9.5–19.1
	–
	1430.0

	1473.2mm
	1474.8
	1471.6
	63.5
	64.29
	61.9
	14.3
	1458.7
	1457.2
	9.5–19.1
	–
	1480.8



AGS ROLL GROOVE SPECIFICATIONS 
For Carbon Steel Pipe And S.S Pipe[image: ]
--Organized By WELPING & GruvMaster


	Actual Pipe Outside Diameter mm
	Dimensions - millimeters (mm)

	
	Pipe Outside Diameter
	Gasket Seat “A”
	Groove Width “B”
	Groove Diameter “C”
	Norminal Wall Thickness for Grooving "T"
	Max. Allow. Flare Dia. “F”

	
	Max.
	Min.
	Basic
	Max.
	Min.
	
	Max.
	Min.
	Carbon Steel
	S.S Steel Sch.10S
	

	1524.0mm
	1525.6
	1522.4
	63.5
	64.29
	61.9
	14.3
	1509.5
	1508.0
	9.5–19.1
	–
	1531.6

	1574.8mm
	1576.4
	1573.2
	63.5
	64.29
	61.9
	14.3
	1560.3
	1558.8
	9.5–19.1
	–
	1582.4

	1625.6mm
	1627.2
	1624.0
	63.5
	64.29
	61.9
	14.3
	1611.1
	1609.6
	12.7–19.1
	–
	1633.2

	1676.4mm
	1678.0
	1674.8
	63.5
	64.29
	61.9
	14.3
	1661.9
	1660.4
	12.7–19.1
	–
	1684.0

	1727.2mm
	1728.8
	1725.6
	63.5
	64.29
	61.9
	14.3
	1712.7
	1711.2
	12.7–19.1
	–
	1734.8

	1828.8mm
	1830.4
	1827.2
	63.5
	64.29
	61.9
	14.3
	1814.3
	1812.8
	12.7–19.1
	–
	1836.4

	1981.2mm
	1982.8
	1979.6
	63.5
	64.29
	61.9
	14.3
	1966.7
	1965.2
	12.7–19.1
	–
	1990.3
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Advanced Groove System (AGS) Groove Specifications


1
WELPING-AGS-Ver.2.0   11/2025


image3.png
[

'4/
.‘




image1.png
GRUI/




image2.png
W WeELPING




