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OGS ROLL GROOVE SPECIFICATIONS 
For Carbon Steel Pipe And All Materials
--Organized By WELPING & GruvMaster


	Actual Pipe Outside Diameter mm
	Dimensions - millimeters

	
	Pipe Outside Diameter
	Gasket Seat “A”
	Groove Width “B”
	Groove Diameter “C”
	Groove Depth “D”
(ref)
	Min. Allow. Wall Thick “T”
	Max. Allow. Flare Dia. “F”

	
	Max.
	Min.
	Basic
	Max.
	Min.
	Basic
	Max.
	Min.
	Max.
	Min.
	
	
	

	33.7mm
	34.11
	33.02
	15.88
	16.64
	15.12
	7.14
	7.9
	6.38
	30.23
	29.85
	1.6
	1.65
	34.5

	42.4mm
	42.9
	41.8
	15.88
	16.64
	15.12
	7.14
	7.9
	6.38
	38.99
	38.61
	1.6
	1.65
	45

	48.3mm
	48.78
	47.78
	15.88
	16.64
	15.12
	7.14
	7.9
	6.38
	45.09
	44.71
	1.6
	1.65
	51.1

	57.0mm
	57.61
	56.39
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	53.85
	53.47
	1.60
	1.65
	59.7

	60.3mm
	60.91
	59.69
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	57.15
	56.77
	1.60
	1.65
	63 0

	73.0mm
	73.74
	72.26
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	69.09
	68.63
	1.98
	2.11
	75.7

	76.1mm
	76.86
	75.34
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	72.26
	71.8
	1.98
	2.11
	78.7

	88.9mm
	89.79
	88.11
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	84.94
	84.48
	1.98
	2.11
	91.4

	101.6mm
	101.62
	100.81
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	97.38
	96.87
	2.11
	2.11
	104.1

	108.0mm
	109.09
	107.21
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	103.73
	103.22
	2.11
	2.11
	110.5

	114.3mm
	115.44
	113.51
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	110.08
	109.57
	2.11
	2.11
	116.8

	127.0mm
	128.27
	126.21
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	122.78
	122.27
	2.11
	2.41
	129.5

	133.0mm
	134.35
	132.21
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	129.13
	128.62
	2.11
	2.77
	135.9

	139.7mm
	141.12
	138.91
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	135.48
	134.97
	2.11
	2.77
	142.2

	141.3mm
	142.72
	140.51
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	137.03
	136.47
	2.13
	2.77
	143.8

	152.4mm
	153.82
	151.61
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	148.08
	147.52
	2.16
	2.77
	154.9

	159.0mm
	160.6
	158.21
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	154.68
	154.12
	2.16
	2.77
	161.3

	165.1mm
	166.7
	164.31
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	160.9
	160.34
	2.16
	2.77
	167.6

	168.3mm
	169.9
	167.51
	15.88
	16.64
	15.12
	8.74
	9.5
	7.98
	163.96
	163.4
	2.16
	2.77
	170.9

	203.2mm
	204.8
	202.41
	19.05
	19.81
	18.29
	11.91
	12.67
	11.15
	198.53
	197.89
	2.34
	2.77
	207.5

	216.3mm
	217.9
	215.51
	19.05
	19.81
	18.29
	11.91
	12.67
	11.15
	211.61
	210.97
	2.34
	2.77
	220.7

	219.1mm
	220.7
	218.31
	19.05
	19.81
	18.29
	11.91
	12.67
	11.15
	214.4
	213.76
	2.34
	2.77
	223.5

	254.0mm
	255.6
	253.21
	19.05
	19.81
	18.29
	11.91
	12.67
	11.15
	249.23
	248.54
	2.39
	3.4
	258.3

	267.4mm
	269.0
	266.61
	19.05
	19.81
	18.29
	11.91
	12.67
	11.15
	262.6
	261.91
	2.39
	3.4
	271.8

	273.0mm
	274.6
	272.21
	19.05
	19.81
	18.29
	11.91
	12.67
	11.15
	268.28
	267.59
	2.39
	3.4
	277.4

	304.8mm
	306.4
	304.01
	19.05
	19.81
	18.29
	11.91
	12.67
	11.15
	299.24
	298.48
	2.77
	3.96
	309.1

	318.5mm
	320.1
	317.71
	19.05
	19.81
	18.29
	11.91
	12.67
	11.15
	312.90
	312.14
	2.77
	3.96
	322.8

	323.9mm
	325.5
	323.11
	19.05
	19.81
	18.29
	11.91
	12.67
	11.15
	318.29
	317.53
	2.77
	3.96
	328.2

	355.6mm
	357.2
	354.81
	23.83
	24.59
	23.07
	11.91
	12.67
	11.15
	350.04
	349.28
	2.77
	3.96
	359.7

	377.0mm
	378.6
	376.21
	23.83
	24.59
	23.07
	11.91
	12.67
	11.15
	371.44
	370.68
	2.77
	4.19
	381.1
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OGS ROLL GROOVE SPECIFICATIONS 
For Carbon Steel Pipe And All Materials
--Organized By WELPING & GruvMaster


	Actual Pipe Outside Diameter mm
	Dimensions - millimeters

	
	Pipe Outside Diameter
	Gasket Seat “A”
	Groove Width “B”
	Groove Diameter “C”
	Groove Depth “D”
(ref)
	Min. Allow. Wall Thick “T”
	Max. Allow. Flare Dia. “F”

	
	Max.
	Min.
	Basic
	Max.
	Min.
	Basic
	Max.
	Min.
	Max.
	Min.
	
	
	

	381.0mm
	382.6
	379.4
	23.83
	24.59
	23.07
	11.91
	12.67
	11.15
	375.44
	374.68
	2.77
	4.19
	385.1

	406.4mm
	[bookmark: _GoBack]408.0
	405.61
	23.83
	24.59
	23.07
	11.91
	12.67
	11.15
	400.84
	400.08
	2.77
	4.19
	410.5

	457.2mm
	455.6
	453.21
	25.4
	26.16
	24.64
	11.91
	12.67
	11.15
	451.64
	450.88
	2.77
	4.19
	461.3

	508mm
	506.4
	504.01
	25.4
	26.16
	24.64
	11.91
	12.67
	11.15
	502.44
	501.68
	2.77
	4.78
	512.1

	559mm
	557.4
	555.01
	25.4
	26.16
	24.64
	12.7
	13.46
	11.94
	550.06
	549.3
	4.37
	4.78
	563.9

	610mm
	611.6
	609.21
	25.4
	26.16
	24.64
	12.7
	13.46
	11.94
	600.86
	600.1
	4.37
	5.54
	614.7

	660.4mm
	662.76
	659.61
	44.45
	45.21
	43.69
	15.88
	16.64
	15.12
	647.7
	646.1
	6.35
	6.35
	665.5

	711.0mm
	713.36
	710.21
	44.45
	45.21
	43.69
	15.88
	16.64
	15.12
	698.5
	696.9
	6.35
	6.35
	716.3

	762.0mm
	764.36
	761.21
	44.45
	45.21
	43.69
	15.88
	16.64
	15.12
	749.3
	747.7
	6.35
	6.35
	767.1

	813.0mm
	815.36
	812.21
	44.45
	45.21
	43.69
	15.88
	16.64
	15.12
	800.1
	798.5
	6.35
	6.35
	817.9

	914.0mm
	916.36
	913.21
	44.45
	45.21
	43.69
	15.88
	16.64
	15.12
	901.7
	900.1
	6.35
	6.35
	919.5

	1067.0mm
	1069.36
	1066.21
	50.8
	51.56
	50.04
	15.88
	16.64
	15.12
	1054.1
	1052.5
	6.35
	6.35
	1071.8
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Original Groove System (OGS) Groove Specifications
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